# SHORT-CIRCUIT AND COORDINATION STUDY AND ARC FLASH HAZARD ANALYSIS

# FOR

# AT&T

Drexel Central Office

1207 South Sheridan Road, Tulsa, OK

geoloc: K54015

clli: KSCYks10

| Study Date | 01-05-2024 |  | [Engineer Seal] |
| --- | --- | --- | --- |
| Revision | [Status] |  |  |
| Engineer | M. Brandon Buscher, PE Lee and Browne Consulting Engineers, Inc. 1207 South Sheridan Road Tulsa, OK 74112-5405 (918) 836-0271 |  |  |
| Lee and Browne Project Number |  | 7041 |  |

TABLE of Contents

SECTION 1 – INTRODUCTION	1

1.1 GENERAL	1

1.2 EXECUTIVE SUMMARY	1

1.3 POWER DISTRIBUTION	2

1.4 ANALYSIS METHODOLOGY	2

1.5 RECOMMENDATIONS	3

1.6 DISCLAIMER	3

SECTION 2 – SYSTEM MODES OF OPERATION	4

2.1 GENERAL	4

2.2 ASSUMPTIONS	4

2.3 SCENARIOS	4

SECTION 3 – SHORT CIRCUIT STUDY	5

3.1 GENERAL	5

3.2 RESULTS	5

3.3 LOW VOLTAGE MOMENTARY REPORT	6

3.4 EQUIPMENT DUTY RATING VIOLATIONS	6

SECTION 4 – COORDINATION STUDY	7

4.1 GENERAL	7

4.2 RESULTS	7

4.3 PROTECTIVE DEVICES LIST – ADJUSTABLE TRIP BREAKERS	8

4.4 PROTECTIVE DEVICES LIST – THERMAL MAGNETIC BREAKER SETTINGS	8

4.5 PROTECTIVE DEVICES LIST – FUSES	9

4.6 TIME CURRENT CURVES	9

SECTION 5 – ARC FLASH HAZARD STUDY	10

5.1 GENERAL	10

5.2 NFPA 70E – INFORMATIVE ANNEX H – TABLE H.3	11

5.3 RESULTS	12

5.4 ARC FLASH HAZARD COMPARISON REPORT	13

SECTION 6 – ATTACHMENTS	14

# INTRODUCTION

## GENERAL

This report documents the short-circuit and arc flash hazard analysis for the AT&T Drexel Central Office located at 1207 South Sheridan Road, Tulsa, OK.  All studies were performed using EasyPower for Windows.  This report supersedes and invalidates results from any study for the scope of equipment being reviewed.

The below table summarizes the pertinent software version and editions of codes and standards utilized in the modeling and performance of this study:

| Resource Description | Version |
| --- | --- |
| EasyPower | 2025 |
| NEC (NFPA 70) | 2023 |
| NFPA 70E | 2018 |
| IEEE 1584 | 2018 |
| AT&T Practice REO-50-08-02-ATP-01 | Version 1.2 05/19/2019 |

Note: the results of this report are based on the system in the specific configuration represented by the attached electrical one-line diagram.  Modification of equipment, changes to system configuration, adjustment of protective device settings, or failure to properly maintain equipment may invalidate these results

## EXECUTIVE SUMMARY

The intent of this report is to provide a tool to supplement an electrical safety program and identify potential issues within a facility’s power system.  The report evaluates the ratings and arc flash safety of the electrical system for AT&T’s Drexel Central Office.

The 5 major parts of this document are as follows:

- System Modes of Operation – Potential configurations of the power system are considered and described in this section of the report.  Each of these scenarios will be studied to confirm that the equipment is rated adequately for the installation and to highlight any arc flash safety issues.

- Short Circuit Study – The model is set up for each possible scenario and a short circuit is modeled at each piece of equipment.  Depending on the strength of the utility and the location of each piece of equipment, the fault current caused by a short circuit will differ.  This study is to verify that the equipment installed is adequately rated to handle a short circuit.

- Coordination Study – The settings of every breaker and fuse in the study scope are verified for the installation in this section.  In addition to selecting trip settings to protect the equipment, settings are selected to provide coordinated behavior during an abnormal condition.  In an ideal situation, this means that during an overload or a short circuit, only the nearest breaker that is feeding the fault will trip, minimizing the impact on the rest of the power system.  However, it should be noted that in most cases, especially existing facilities, that the ideal case cannot be achieved under all fault conditions.  Coordinating and adjusting these settings also has the potential to reduce the overall arc flash hazard by allowing protective devices to trip as quickly as possible while still being set to allow normal current to flow.

- Arc Flash Hazard Study – this section of the report generates the labels that are affixed to equipment in the field.  The labels quantify the energy that could be released during an arc flash event as well as the minimum safe distance a person would need to maintain to only receive second degree burns on exposed skin.  In some cases, the energy is greater than 40 cal/cm² and cannot be reduced any further.  These cases are highlighted for future mitigation.

- Attachments – the documents appended to the end of the report contain information obtained during the study, observed code violations, simulation data, and copies of the arc flash labels.

## POWER DISTRIBUTION

The power distribution system for this site consists of:

- One 750kVA commercial utility feed and an 800kW standby generator.

- The EPSS contains 2 bypass-isolation type ATS’s in the system.

- The power distribution for the entire building is backed by the EPSS.

## ANALYSIS METHODOLOGY

Lee and Browne’s arc flash hazard analysis of the power system is performed in accordance with the recommendations of IEEE-1584.  A complete process is provided within this standard for use in properly applying the calculation models that are coded into analysis software such as EasyPower.

The general steps involved in the IEEE-1584 analysis found in clause 6 are listed below.

- Collect the system and installation data

- Determine the system modes of operation

- Determine the bolted fault currents

- Determine typical gap and enclosure size based upon system voltages and classes of equipment

- Determine the equipment electrode configuration

- Determine the working distance

- Calculate arcing current

- Determine arc duration

- Calculate incident energy

- Determine the arc-flash boundary for all equipment

These steps apply to arc flash calculation, but this methodology of modeling the power system also applies to short circuit and coordination studies as well.

## RECOMMENDATIONS

Note: The recommendations included in this report are based on the power system after all device setting modifications have been completed per the recommendations contained herein.

As part of the analysis of the power system, equipment ratings and potential hazards are identified and presented in this study.  Primary topics of concern are:

- Equipment installed that is not adequately rated for the available short circuit current in the power system

- Equipment which has an arc flash incident energy level greater than 40 cal/cm²

- General code violations that were observed during data collection and survey.

Equipment that is not adequately rated for the available fault current are identified in section 3.2 of this report. The equipment listed as being overdutied in section 3.2 will need to be addressed by the owner as part of a fault duty remediation effort.

The results of the arc flash hazard analysis, included in section 5.3 of this report, show both the calculated arc flash incident energy and the arc flash boundary distances at each bus in the study.  These results are dependent on the coordination study performed as part of section 5 of this report.  Equipment that generates an arc flash incident energy greater than 40 cal/cm² are identified for owner consideration and follow-up with arc flash mitigation.

Note that the arc flash hazard analysis and recommended PPE levels are no substitute for safe work practices.  Burn injuries can occur even when adequate PPE is employed.  The recommended PPE may do little to protect against debris and other effects associated with an arc blast.  Protection from an arc flash can best be provided by working only on circuits or equipment that have been placed into an electrically safe state.  Work should never be performed on or near equipment marked as arc flash dangerous unless it has been put into a safe state.

General code violations observed during the data collection and survey phases of this project are included in section 6.4.

## DISCLAIMER

The following report was prepared by Lee and Browne Consulting Engineers, Inc. utilizing industry-accepted standards, practices, methods, and analysis tools.  Data used in this analysis was acquired by Lee and Browne and provided by others, through onsite investigation, published information, equipment nameplates, manufacturer ratings, analysis, or other means.

The recommendations contained herein are based on past experience, our professional opinion, and the implementation of the recommendations provided herein.  Lee and Browne assumes no responsibility for inaccuracies in data provided by others.

The study is intended for use by qualified individuals to facilitate the installation, operation, maintenance, and safety of the power system considered in this report.  Modification of equipment, changes to system configuration, adjustment of protective device settings, or failure to properly maintain equipment may invalidate these results.

No recommendations or suggestions for the overall power system are made beyond the specific equipment indicated within this report.

# SYSTEM MODES OF OPERATION

## GENERAL

This section describes the possible operating modes of the system.  Each scenario considered in Section 2.3 below represents a different configuration of power sources and load connectivity with unique fault current and arc flash hazards.

Since the purpose of the short circuit and arc flash study is to determine the worst-case results, in buildings with multiple ATS’s, only configurations all ATS’s fed from the same sources are considered.  This is intentional because the maximum potential fault current should occur when all sources and motors are feeding into a given fault.

Scenarios such as a fault occurring at an ATS during the middle of a 500 millisecond or less closed transition transfer are not considered in this analysis.  This is because such a scenario is well outside of any typical operating parameters.  By considering such events, unrealistic fault current levels would drive PPE requirements higher and potentially creating more risk due to reduced dexterity of workers.

## ASSUMPTIONS

- All equipment has been properly maintained and is in good operational condition and working order.

- When motor contribution is considered, all motors are in the on state at the time of a fault.

- The base power system information contained in the EasyPower model provided for use in this project has been correctly entered and is correct.

## SCENARIOS

The following operating scenarios are considered in the study.  Results are presented for each scenario with the worst-case values being used in determining minimum acceptable equipment ratings and arc flash hazard.

- All ATS’s on utility power source.

- All ATS’s on generator power source.

# SHORT CIRCUIT STUDY

## GENERAL

An electrical system short-circuit analysis is used for the following:

    - To compare the calculated maximum fault currents with interrupting ratings of overcurrent protective devices, such as circuit breakers and fuses.

    - To verify the adequacy of equipment and bussing to withstand the effects of the calculated maximum fault current levels.

    - To assist in the selection of overcurrent protective device settings.

    - To serve as the base model for use in calculating arc flash hazard and incident energy for the components within the system.

EasyPower calculates the maximum available, three-phase, RMS symmetrical, short-circuit amperes at each piece of equipment in the system.  The results are based on user input data, such as utility maximum fault current, wire sizes and lengths, transformer impedance, fuse sizes and types, etc.

Electrical distribution systems must be able to withstand and/or interrupt the worst-case fault current that it may be subjected to.  NEC 110.9 requires circuit breakers to have a rating sufficient for interrupting the maximum available fault current present at their line-side terminals.  Devices which are not sufficiently rated to interrupt the maximum fault current should be remediated.  Devices to consider for remediation are highlighted in the study results in this report.

## RESULTS

This project contains arc flash hazard mitigation scope only, meaning that fault duty remediation should work should already be complete.  Based on the electrical model and information provided from the previous fault duty remediation scope, there is no overdutied equipment.  This means that all equipment in the building should be adequately rated for the worst-case potential short circuit condition.

The full results of the short circuit study are presented below in Section 3.3 LOW VOLTAGE MOMENTARY REPORT. If any overdutied equipment was identified, it is repeated separately in Section 3.4 EQUIPMENT DUTY RATING VIOLATIONS.

## LOW VOLTAGE MOMENTARY REPORT

## EQUIPMENT DUTY RATING VIOLATIONS

# COORDINATION STUDY

## GENERAL

Each protective device in the model is considered to determine the baseline settings that will adequately protect the equipment or wiring that it serves.  This means that the device must be rated for the maximum possible short circuit it could experience and must allow the normal flow of current without interrupting the circuit.  However, during an abnormal condition, such as a fault or overload, the device must be set sensitively enough to detect it and open the circuit to minimize potential damage.  This is performed using the equipment and device characteristic library provided by manufacturers and included with EasyPower.

The coordination study evaluates the behavior between protective devices in the power system and optimizes their settings.  This is to provide the most coordinated response possible while also considering potential arc-flash risks.

Proper coordination of the protective devices in the power system minimizes the impact of an overcurrent event on the rest of the power system.  In an ideally coordinated system, any fault would only trip the nearest protective device that feeds the wire or equipment experiencing the fault.  Such a system is said to be selectively coordinated.  In most scenarios, it is not possible to achieve a fully coordinated system – either due to equipment restrictions, practicality, or limitations of existing hardware.

In scenarios where selectivity is not required, it is sometimes possible to reduce the available incident energy of an arc flash event by sacrificing some degree of selectivity.  Cases where such recommendations are made are described in the results of this section of the report.

Wherever the feature is installed, ground fault protective functions are considered and shown on the time current curves as well.  In cases with many devices being considered at once, the ground fault protection may be shown on a separate diagram for clarity.

## RESULTS

The protective device settings of the power system are split based on circuit breaker/fuse type and included in this section of the report.  Any trip settings or ratings to be changed are highlighted in the following section for ease of reference.

As part of the system configuration, adjustments were made at the incoming equipment to mitigate arc flash hazard.  After coordination, the only arc flash hazards that remain are at the main service switchgear and the generator equipment and switchgear.  The new values of the protective device adjustments are highlighted in the following tables.  These adjustments must be made in the field in order for the arc flash study results to be valid.

## PROTECTIVE DEVICES LIST – ADJUSTABLE TRIP BREAKERS

## PROTECTIVE DEVICES LIST – THERMAL MAGNETIC BREAKER SETTINGS

## PROTECTIVE DEVICES LIST – FUSES

## TIME CURRENT CURVES

Time current curves of all elements modeled in the system are included at the end of this report as section 6.7.

# ARC FLASH HAZARD STUDY

## GENERAL

An Arc Flash Hazard Analysis is intended to assist qualified personnel who interact with energized electrical equipment in determining the appropriate PPE required while working with live electrical equipment where there is a potential exposure to arc flash events.  The calculated incident energy is determined based on several factors, including the system configuration, available fault current at the point of the arc, and the amount of time required for the system’s protective devices to clear the fault.  An upper limit is applied to the arcing time by the software as the anticipated maximum amount of time that a person would be exposed to the hazard.

The calculations are completed using EasyPower’s arc flash module based on the latest version of IEEE 1584, “IEEE Guide for Performing Arc-Flash Hazard Calculations”.  They are also based on the data collected from limited field survey, owner/contractor provided documentation, manufacturer data, etc.

The results of this analysis are only valid for the system configuration in the state shown in the one-line diagram.  The study should be updated any time that there is a change to the system configuration, equipment upgrades, protective device settings, or safety requirements.  The PPE required shall also be considered based on the latest edition of NFPA 70E, “Standard for Electrical Safety in the Workplace”.

Whenever possible, equipment should be deenergized prior to performing any work.  If it is not possible to deenergize the equipment prior to performing work, every safety precaution should be taken to ensure a safe work environment.  All work must be completed only by qualified and trained personnel.

Information was compiled for equipment, available fault current, feeder lengths, etc. to determine the protective device settings and available fault current at each location within the scope of work.  IEEE-1584 provides a comprehensive method for arc flash hazard analysis.  The calculations used are based on extensive testing carried out on low and medium voltage systems and is applicable to a wide range of power systems.

The results presented in this report are based solely on the IEEE-1584 calculation method.  The IEEE-1584 method is applicable only to three-phase arcing faults, though single-phase or phase-to-phase faults are expected to quickly escalate to three-phase faults.  For single-phase systems, the three-phase results provide a conservative estimate of the incident energy available.  The calculations also do not consider the hazards from other byproducts of the arc flash, such as an arc blast or flying debris, shrapnel, or vaporized and molten metals.

The results of this study assume that the protective devices are all in good working order and have been properly maintained to still function within specified tolerances.  Non-functioning overcurrent protective devices can allow arcing faults to persist for much longer than the calculations would show, producing much higher incident energies and much more severe arc flash hazards than presented in this report.  It is critical that proper maintenance be performed on the electrical equipment within the power system, otherwise the results of this report will be invalidated.

## NFPA 70E – INFORMATIVE ANNEX H – TABLE H.3

Data excerpted from NFPA 70E, 2018 Edition.

| Table H.3 Summary of Specific Sections Describing PPE for Electrical Hazards |  |  |
| --- | --- | --- |
| Shock Hazard PPE |  | Applicable Section(s) |
| Rubber insulating gloves and leather protectors, unless the requirements of ASTM F496 are met |  | 130.7(C)(7)(a) |
| Rubber insulating sleeves as needed |  | 130.7(C)(7)(a) |
| Class G or E hard hat as needed |  | 130.7(C)(3) |
| Safety glasses or goggles as needed |  | 130.7(C)(4) |
| Dielectric overshoes as needed |  | 130.7(C)(8) |
| Incident Energy Exposures Greater than or Equal to 1.2 cal/cm² (5 J/cm²) |  |  |
| Clothing: |  | 130.7(C)(1), 130.7(C)(2), 130.7(C)(6), 130.7(C)(7), 130.7(C)(9)(d) |
|  | Arc-rated clothing system with an arc rating appropriate to the anticipated incident energy exposure |  |
| Clothing underlayers (when used): |  | 130.7(C)(9)(c), 130.7(C)(11), 130.7(C)(12) |
|  | Arc-rated or nonmelting untreated natural fiber |  |
| Gloves: |  | 130.7(C)(7)(b), 130.7(C)(10)(d) |
|  | Exposures greater than or equal to 1.2 cal/cm² (5 J/cm²) and less than or equal to 8 cal/cm² (33.5 J/cm²): heavy-duty leather gloves |  |
|  | Exposures greater than 8 cal/cm² (33.5 J/cm²): rubber insulating gloves with their leather protectors or arc-rated gloves |  |
| Hard hat: |  | 130.7(C)(1), 130.7(C)(3) |
|  | Class G or E |  |
| Face Shield: |  | 130.7(C)(1), 130.7(C)(3), 130.7(C)(10)(a), 130.7(C)(10)(b), 130.7(C)(10)(c) |
|  | Exposures greater than or equal to 1.2 cal/cm² (5 J/cm²) and less than or equal to 12 cal/cm² (50.2 J/cm²): Arc-rated face shield that covers the face, neck, and chin and an arc-rated balaclava or an arc-rated arc flash suit hood |  |
|  | Exposures greater than 12 cal/cm² (50.2 J/cm²): arc-rated flash suit hood |  |
| Safety glasses or goggles |  | 130.7(C)(4), 130.7(C)(10)(c) |
| Hearing Protection |  | 130.7(C)(5) |
| Footwear: |  | 130.7(C)(10)(e) |
|  | Exposures greater than or equal to 1.2 cal/cm² (5 J/cm²) and less than or equal to 4 cal/cm² (16.75 J/cm²): Heavy-duty leather footwear (as needed) |  |
|  | Exposures greater than 4 cal/cm² (16.75 J/cm²): Heavy-duty leather footwear |  |

## RESULTS

The following equipment was identified as having an incident energy greater than 40 cal/cm² even after completion of the recommended overcurrent protective device settings are made.  These items will be identified in the arc flash hazard equipment summary with an “Extreme Danger” PPE level and with “DANGER” labels with a red banner as opposed to the typical orange banner.  For more details on the labels, see Section 6.6 - ARC FLASH LABELS.

The full list of arc flash hazard results is included on the following pages.

## ARC FLASH HAZARD COMPARISON REPORT

# ATTACHMENTS

## UTILITY INFORMATION

## SINGLE-LINE DIAGRAM

## RECOMMENDED SETTINGS REPAIR RECORD(S)

## TABLE 6: NEC CODE VIOLATIONS

## TABLE 7: REMEDIATION & MITIGATION DEVICE SUMMARY

## ARC FLASH LABELS

## TIME CURRENT CURVES

# UTILITY INFORMATION

# SINGLE-LINE DIAGRAM

# RECOMMENDED SETTINGS REPAIR RECORD(S)

Infrared scanning was performed by an electrical contractor as part of the study process.  The complete report has been submitted to AT&T for distribution to property management for their records.  Pertinent pages of the report are included in this section to bring items needing repair to AT&T’s attention.

# TABLE 6: NEC CODE VIOLATIONS

NO CODE VIOLATIONS WERE OBSERVED AT THIS SITE.

# TABLE 7: REMEDIATION & MITIGATION DEVICE SUMMARY

# ARC FLASH LABELS

# TIME CURRENT CURVES